المملكة العربية السعودية

وزارة التعليم العالي

جامعة الملك عبدالعزيز

وكالة الجامعة

للدراسات العليا والبحث العلمي

مجلس البحث العلمي

KINGDOM OF SAUDI ARABIA

Ministry of Higher Education

KING ABDULAZIZ UNIVERSITY

Office of the Vice Presidency

Post-Graduate Studies & Academic Research

SEIENTIFIC RESEARCH COUNCIL

www.kaau.edu.sa/src

COVER PAGE

Final Report

Name of College: College of Engineering

Name of Department: Department of Thermal Engineering & Desalination Technology

Title of Research : APPLICATION OF PHASE CHANGE MATERIALS FOR BUILDING INSULATION TO REDUCE COOLING LOADS

Final Report for Project No.: (424/105)

Duration of the project for which the report is written : Nine Months

Names of the Investigator (s) :

-Principal Investigator: Dr. Majed M. Alhazmy

-Co-Investigator: Prof. Ali Elbahi

-Co-Investigator: Prof. Galal M. Zaki

-Co-Investigator:

-Co-Investigator:

Date of Submission of this report : 29/ 12/ 1425 H

ملخص تقرير نهائي  ( عربي )

المملكة العربية السعودية

وزارة التعليم العالي

جامعة الملك عبدالعزيز

وكالة الجامعة

للدراسات العليا والبحث العلمي

مجلس البحث العلمي

KINGDOM OF SAUDI ARABIA

Ministry of Higher Education

KING ABDULAZIZ UNIVERSITY

Office of the Vice Presidency

Post-Graduate Studies & Academic Research

SEIENTIFIC RESEARCH COUNCIL

1- عنوان البحث : استخدام مواد متغيرة الطور كعازل حراري في المباني لتخفيض الطاقة المستخدمة في التكييف

2 – الباحث الرئيسي: د. ماجد بن معلا الحازمي

3- أسم الكلية: الهندسة

4- أسم القسم: الهندسة الحرارية و تقنية تحلية المياه

الملخص يهتم هذا البحث بتطوير طريقة جديدة لعزل المباني حراريا بهدف تقليل الطاقة المستخدمة في تكييف الهواء بالمباني، ففي الجزء الأول يستعرض التقرير أهمية توفير الطاقة في المملكة العربية السعودية، إضافة إلى استعراض أهم الطرق المستخدمة في عزل المباني و طرق قياس معامل التوصيل الحراري في المواد الصلبة. و قد تمت مراجعة أهم الأبحاث الخاصة باستخدام مواد متغيرة الطور بهدف استخدامها لإنشاء طبقة تختزن الحرارة أثناء النهار و تطلقها خلال الليل و اتضح من هذه المراجعة أن جميع التطبيقات الحالية هي لتخزين الطاقة و ليس لمنع انتقالها و كذلك صعوبة القيام بتحليل رياضي لعملية تغير الطور و ذلك بسبب وجود ما يسمى الطبقة الحدية الحرة. و لتقييم طرق العزل الحراري الحالية و التي تستخدم فيها قطع من مادة البوليسترين لملء الفراغات الموجودة داخل قوالب طوب البناء فلقد تمت معالجة و حدة بناء ٢٠ ×٢٠×٢٠سم بها تسع فتحات مربعة كل منها ٥×٥×٢٠سم رياضيا. حيث تم عمل نموذج رياضي يشتمل على معادلات انتقال الحرارة بالحمل و التوصيل الحراري في جدران الطوب‘ و بين التحليل الرياضي أن تيارات الهواء الداخلية تساعد على انتقال الحرارة خلال جدران المباني، وأن طريقة العزل المستخدمة حاليا بوضع قطع من مادة البوليسترين ساعد في تخفيض الحمل الحراري بنسبة ١٥% فقط و عند إجراء التجارب على وحدة بناء و صلت نسبة انخفاض الحمل الحراري بسبب استخدام البوليستسرين إلى ٢٦%. بدأت دراسة استخدام مواد متغيرة الطور بتحليل رياضي لانتقال الحرارة في شريحة عند تعرض سطحها إلى درجة حرارة متغيرة مع الزمن تماثل تغير ظروف الجو الخارجي و على ضوء هذه الدراسة و باستخدام شمع من نوع Rubitherm RT 42 درجة انصهارها ٤٣ ٥م و تم اختيار سمك العازل الشمعي بحيث يكون أقل من ٣٠مم، أجريت بعد ذلك قياسات معملية على وحدة شمعية ١٥×١٥×٢٥مم٣ تم رفع درجة حرارتها بواسطة مصدر ضوئي قدرة ٦٥۰ وات و لوحظ وصول الشمع إلى درجات تحميص عالية و هو ما يجب تجنبه عند تطوير كبسولات الشمع، تم تصنيع ثلاث كبسولات من نفس نوع الشمع مقاس كل منها ٢×٥×٢٠ سم٣ و وضعت داخل فتحات و حدة البناء و تم تسخينها، أوضحت القياسات أن درجة حرارة السطح الساخن بلغت ٨‚٦۰ ٥م في حالة وحدات البناء بوجود فراغات الهواء و ارتفعت إلى ٧‚٦٧ ٥م بوجود مادة البوليستيرين و انخفضت إلى ٥٣ ٥م في حالة استخدام كبسولات الشمع، في جميع التجارب كانت شدة الضوء الساقط على السطح الساخن من و حدة البناء ١٠٧٠وات/م٢ و كان السطح البارد معرضاً للتبريد بالحمل الحر.

KINGDOM OF SAUDI ARABIA Ministry of Higher Education KING ABDULAZIZ UNIVERSITY Office of the Vice Presidency Post-Graduate Studies & Academic Research SEIENTIFIC RESEARCH COUNCIL المملكة العربية السعودية وزارة التعليم العالي جامعة الملك عبدالعزيز وكالة الجامعة للدراسات العليا والبحث العلمي مجلس البحث العلمي FINAL SUMMARY (English)

1. Title of Project: APPLICATION OF PHASE CHANGE MATERIALS FOR BUILDING INSULATION TO REDUCE COOLING LOADS

2 Principal Investigator: Dr. Majed M. Alhazmy

3. Name of the College: College of Engineering

4. Name of the Department: Department of Thermal Engineering & Desalination Technology

SUMMARY This project is concerned with developing a new technique for insulation of buildings. The first part of the report discusses the importance of using building insulation in the Kingdom of Saudi Arabia. A review of the important insulation techniques along with the methods for thermal conductivity measurements are presented. The available literature in the field of phase change materials (PCMs) have been reviewed in order to utilize such materials in forming an insulation layer that would store heat during day time and release it to the ambient during the night time. Most of the literature is found to be concerned with using PCMs as a storing medium not as a an insulation (barrier) system. It is found that developing a mathematical model for such materials is an involved task due to presence of the so called free boundary layer. In order to evaluate the currently used insulation techniques that use polystyrene bars to fill the holes in buildings bricks a mathematical model was developed. A building brick of 20x20x20 cm with nine holes was modeled. Each hole is 5x5x20 cm. The model shows that internal convection currents help in transferring heat through the brick and the polystyrene bars stop such convection. Comparing the air cavities with polystyrene filled cavities showed that the latter reduces the heat transfer through the brick by 15% (relative to air cavities). Experimental analysis showed that a reduction of 26% can be reached. The part concerning using the PCMs started by solving the problem of heat transfer though a PCM slab of 15x15x25 cm of a wax manufactured by Rubitherm company of Germany having a melting point temperature of 43oC. The slab thickness was selected to be 30mm. An experimental measurement was performed on the selected PCM when subjected to a light source of 650W/m2. The PCM temperature reached a high degree of superheating which should be avoided when the PCM capsules are made. Three identical capsules have been made and installed with in a building brick. When heating the brick by a light source of 1070W/m2 the hot side of brick with air cavities reached 60.8oC. This value increases to 67.7oC when polystyrene bars are installed and reduces to 53oC with PCM capsules. In all experiments the cold side of the brick maintained its temperature by free convection.